## Pump Monitoring
Address | Register name | Scale | Description
207 | ActualSetpointManualHI | 0.1 ml/h | The actual setpoint used in operating mode "Manual".
208 | ActualSetpointManualLO |  | Can be set via SetpointManual (register 00106-00107) or via the pump HMI.
209 | ActualPulseVolumeHI | 1 nl | The actual pulse volume used in operating mode "Pulse".
210 | ActualPulseVolumeLO |  | Can be set via SetPulseVolume (register 00108-00109) or via the pump HMI.
The actual batch dosing volume used in operating mode "Batch".
211 | ActualBatchDosingVolumeHI | 0.001 ml | Can be set via SetBatchDosingVolume (register 00110-00111) or via the pump
212 | ActualBatchDosingVolumeLO |  | HMI.
213 | ActualBatchDosingTimeHI | 0.1 s | The actual batch dosing time used in operating mode "Batch".
214 | ActualBatchDosingTimeLO |  | Can be set via SetBatchDosingTime (register 00112-00113) or via the pump HMI.
215 | ActualPressureMax | 0.1 bar | Actual value of (relative) pressure alarm limit setting. Can be set via SetPressureMax (register 00114) or via the pump HMI.
216 | ControlSourceStates | Bits | Status of start/stop control sources, "1" means "Active". They can be active simultaneously. Bit 0: Stop via pump HMI Bit 1: External stop Bit 2: Stop from bus.
217 | FaultCode | Enum
218 | WarningCode | Enum | See section 8.11Alarms and warning.
219 | WarningBits | Bits
220 | DateTimeYear |  | Present value of the internal real-time clock (RTC).
Can be set via SetDateTime (register 00117-00122) or via the pump HMI.
221 | DateTimeMonth |  | Year (from year 2000)
Month [1-12]
Day [1-31]
222 | DateTimeDay | BCD | Hour [0-23]
|  | string | Minute [0-59]
223 | DateTimeHour |  | Second [0-59]
Each byte is a binary-coded decimal (BCD) value.
224 | DateTimeMinute |  | 15:38:00, April 24 2011, is coded with hexadecimal numbers as:
225 | DateTimeSecond |  | Year = 11h, Month = 04h, Day = 24h, Hour = 15h, Minute = 38h, Second = 00h.
301 | DosingPressureMax | Bar | Maximum dosing pressure, fixed factory-set value for this pump type.
302 | DosingCapacityMaxHI | 0.1 ml/h | Maximum dosing capacity, fixed factory-set value for this pump type.
303 | DosingCapacityMaxLO
304 | DosingCapacityReferenceHI | 0.1 ml/h | The dosing capacity setpoint shown in the pump display. It represents the actual
305 | DosingCapacityReferenceLO |  | setpoint belonging to the actual operating mode and dosing state.
306 | MeasuredDosingCapacityHI | 0.1 ml/h | Measured (actual) dosing capacity. FlowControl bit in control register 00102 must be enabled for this value to be available.
307 | MeasuredDosingCapacityLO
308 | MeasuredPressure | 0.1 bar | Measured absolute pressure. FlowControl bit in control register 00102 must be enabled. Except for the atmospheric pressure, it corresponds to "Backpressure" reading in the display.
309 | PulseInputFrequency | 1 Hz | Frequency of pulse input (external pulse input signal or Modbus Pulse command in control register 00103).
310 | RemainingDosingVolumeHI | 0.001 ml | Actual remaining volume to be dosed. Used in "Batch" mode.
311 | RemainingDosingVolumeLO
312 | VolumeTotalHI | 0.001 l | Total volume dosed (non-resettable).
313 | VolumeTotalLO
314 | VolumeTripCounterHI | 0.001 l | Dosed-volume trip counter (reset with ResetVolumeCounter command in control
315 | VolumeTripCounterLO |  | register 00103).
320 | NumberOfPowerOns | - | Counts the number of times the pump has been powered on (non-resettable).
321 | RunTimeHI | 1 | Counts the time the DDA pump has been dosing (non-resettable).
322 | RunTimeLO
323 | OperatingHoursHI | 1 s | Counts the number of hours the DDA pump has been switched on. It counts both
324 | OperatingHoursLO |  | when the pump is dosing and when it is not dosing.
325 | StrokeCounterHI | - | Counts the number of strokes (non-resettable).
326 | StrokeCounterLO
327 | TimeToNextDosingHI | 1 s | Time before the next dosing takes place (only in "Timer" mode).
328 | TimeToNextDosingLO