## Table044 (Page 24)
Event_code | Even_ group | Event_description | Depends on FlowControl enabled | Event action | Auto-acknowledge
210 | Pump head | Maximum pressure limit exceeded. Register 215 | Yes | Alarm | Yes
211 | Pump head | Backpressure too low. Fixed underpressure limit (1.5 bar). | Yes | Alarm/ Warning^{1)} | Yes
35 | Pump head | Air bubbles, gas in pump head, deaerating problem. | Yes | Warning | Yes
208 | Pump head | Cavitation. | Yes | Warning | Yes
36 | Pump head | Discharge (pressure) valve leakage. | Yes | Warning | Yes
37 | Pump head | Suction valve leakage. | Yes | Warning | Yes
12 | Pump head | Service now (time for service exceeded). | No | Warning | No
33 | Pump head | Soon time for service (general service information). | No | Warning | No
17 | Pump head | Flow deviation (performance requirement not met). | Yes | Warning | Yes
51 | Pump head | Blocked motor/pump. | No | Alarm | Yes
206 | Tank | Low level in tank. | No | Warning | Yes
57 | Tank | Empty tank (dry running). | No | Alarm | Yes
169 | Input signals | Cable breakdown on FlowControl. | Yes | Warning | Yes
97 | Input signals | Defective analog 4-20 mA cable. | No | Alarm | Yes
15 | Communication | Modbus communication fault (main network communication fault). | No | Alarm^{2)} | No
152 | Communication | Extension box communication fault (GENIbus communication fault). Defective cable between E-box and DDA pump. | No | Alarm^{2)} | No